## INPUTS
ACC Adiabatic Relief — Simulation Inputs
A PLANT CONFIGURATION
Parameter | Value | Notes
N_CHILLERS | 9 | Number of identical chillers in plant
Q_RAT_KW | 2200 | Rated cooling capacity per chiller (kW)
COP_RAT | 4.8 | Rated COP at rated conditions
T_LET_RAT | 24 | Rated leaving evaporator temp — curve normalisation only (°C)
T_LET_DES | 24 | Operating CHW supply setpoint used in simulation (°C)
T_ODB_RAT | 32 | Rated outdoor dry-bulb temp (°C)
FAN_POWER_KW | 0 | Condenser fan power per chiller — embedded in EIR, typically 0 (kW)
B ADIABATIC RELIEF PARAMETERS
T_SWITCH | 31 | Pad activation threshold — pads ON when T_odb strictly > this (°C)
ETA_SAT | 0.78 | Pad saturation efficiency (0–1); typical 0.65–0.80
COND_INLET_T_OFFSET | 5 | Heat recirculation offset added after pad cooling (°C); 0 for open installation
C OPERATING LIMITS
PLR_MIN | 0.1 | Min PLR threshold — hours below this are flagged (no cutoff applied)
PLR_MIN_CALC | 0.8 | Min PLR used in EIR part-load curve evaluation
COP_MAX | 30 | Hard COP ceiling (enforced as EIR floor = 1/COP_MAX)
D BI-QUADRATIC CURVE COEFFICIENTS
Curve | C00 | C10 | C20 | C01 | C02 | C11 | Notes
CAP_FTT — Capacity vs (T_let, T_odb) | 1.2897 | 0 | 0.0008606 | 0 | -0.0013609 | 0.0020811 | x = T_let (°C), y = T_odb / T_chiller_inlet (°C)
EIR_FTT — EIR vs (T_let, T_odb) | 0.27626 | 0 | -0.00047595 | 0 | 0.0010621 | -0.00011086 | x = T_let (°C), y = T_odb / T_chiller_inlet (°C)
EIR_FPT — EIR vs (PLR, T_odb − T_let) | 0.0014427 | 0.3446 | 0.66003 | 0.00080729 | -5.261e-05 | -0.0011782 | x = PLR, y = T_chiller_inlet − T_let (°C)
E NORMALISATION CONSTANTS (auto-calculated — do not edit)
EIR_RAT |  | Rated EIR = 1 / COP_RAT
dT_RAT |  | Rated condenser-evap temperature difference
C_NORM_CAP |  | CAP_FTT evaluated at rated conditions (should ≈ C_NORM_CAP itself — verify ~1.0 before C_NORM division)
C_NORM_EIR |  | EIR_FTT evaluated at rated conditions
C_NORM_PT |  | EIR_FPT evaluated at PLR=1, dT=dT_RAT

## WEATHER_DATA
|  | Dry-bulb temperature (°C) | Wet-bulb temperature (°C)
|  | <paste EPW filename here> | <paste EPW filename here>
Date | Time | T_odb_C | T_wb_C
← Paste IES VistaPro weather export here (DBT & WBT columns only, 8,760 rows from row 4)

## LOAD_DATA
CHWL total load (kW)
<paste circuit/loop name here>
Date | Time | Q_plant_kW
← Paste IES VistaPro CHWL load export here (column C, 8,760 rows from row 4)

## SIMULATION
Index | Weather |  |  | Adiabatic |  |  |  |  | Demand | Chiller — Adiabatic | [11 empty] | Chiller — Dry Baseline | [10 empty] | Plant Totals |  |  |  | Energy & Savings |  |  |  | Flags |  | Helper
Hour | T_odb_C | T_wb_C | Q_plant_demand_kW | adiabatic_active | T_odb_eff_C | T_depression_C | T_chiller_inlet_C | T_dry_inlet_C | Q_chiller_demand_kW | fCAPtt_adi | Q_cap_chiller_adi | Q_served_adi | Q_unmet_adi | PLR_adi | PLR_calc_adi | fEIRtt_adi | dT_adi | fEIRpt_adi | EIR_adi | COP_adi | P_plant_adi_kW | fCAPtt_dry | Q_cap_chiller_dry | Q_served_dry | PLR_dry | PLR_calc_dry | fEIRtt_dry | dT_dry | fEIRpt_dry | EIR_dry | COP_dry | P_plant_dry_kW | Q_plant_cap_adi_kW | Q_plant_cap_dry_kW | Q_plant_served_kW | Q_plant_unmet_kW | P_saving_kW | E_plant_adi_kWh | E_plant_dry_kWh | E_saving_kWh | over_capacity_flag | low_PLR_flag | month_num
↑ Select row 4 (all columns A:AR), then drag fill handle down to row 8763 (8,760 hours)

## MONTHLY_SUMMARY
Monthly Summary
Month | Month# | E_adi_MWh | E_dry_MWh | E_saving_MWh | Saving_% | Adi_hrs | Avg_COP_adi | Avg_COP_dry | Q_served_MWh | Q_unmet_kWh | Avg_PLR_adi
Jan | 1
Feb | 2
Mar | 3
Apr | 4
May | 5
Jun | 6
Jul | 7
Aug | 8
Sep | 9
Oct | 10
Nov | 11
Dec | 12
TOTAL

## ANNUAL_SUMMARY
Annual Summary — ACC Adiabatic Relief
ENERGY
E_adi_MWh | Total plant energy — adiabatic mode
E_dry_MWh | Total plant energy — dry baseline
E_saving_MWh | Annual energy saving (dry − adiabatic)
Saving_% | Energy saving as % of dry baseline
ADIABATIC OPERATION
Adi_hrs | Hours pads were active
Adi_%_year | Fraction of year pads active
COP — ADIABATIC MODE
Avg_COP_adi
Max_COP_adi
Min_COP_adi
COP — DRY BASELINE
Avg_COP_dry
Max_COP_dry
Min_COP_dry
LOAD COVERAGE
Q_served_MWh | Total cooling delivered
Q_unmet_kWh | Total unmet cooling load
Overcap_hrs | Hours chiller was over-capacity
LowPLR_hrs | Hours PLR below PLR_MIN threshold
VERIFICATION CHECKS
T_eff_below_Twb_count | Should be 0 — T_odb_eff must not go below T_wb
C_NORM_CAP | Capacity curve norm (raw value, pre-division)
C_NORM_EIR | EIR temp curve norm
C_NORM_PT | EIR part-load curve norm